PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 7th November, 2019

F. No. PNGRB/Tech/1-T4SCGD/(1)/2019. – In exercise of the powers conferred by section 61 of the Petroleum and Natural Gas Regulatory Board Act, 2006 (19 of 2006), the Petroleum and Natural Gas Regulatory Board hereby makes the following regulations further to amend the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, namely:-

- Short title and commencement.-

- These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Amendment Regulations, 2019.

- They shall come into force on the date of their publication in the Official Gazette.

- In the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, -

- in regulation 4, for clause (d), the following clause shall be substituted, namely: -

“(d) The CNG Station shall be designed, operated and maintained in line with the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Retail Outlets dispensing Petroleum, Auto LPG and CNG) Regulations, 2018.”;

- in Schedule-1A, under heading “Pipes and tubing for above ground service lines up to meter set assembly”, the paragraph beginning with the words, brackets and letters “Galvanized Iron (GI) pipes” and ending with the words, figure and letters “Schedule I D of these regulations.”, the following paragraph shall be substituted, namely: -

“Galvanized Iron (GI) pipes shall be used in above ground service lines up to consumer meter or meter control valve. The use of copper tubing shall only be after consumer meter such that this is not accessible to third party. Use of copper pipe / tube before consumer meter should be inside the kitchen only. As an alternate to copper pipe/ tube, multi layered composite pipe complying with the requirements of ISO 17484-1 can also be used. GI pipes, copper tubing and multilayer composite pipes shall conform to the requirements given in Annexure-IV of this standard. Use of non-galvanized pipes should be restricted as far as possible; however, in case they are used they shall be properly protected and painted. PE pipe shall not be used for above ground gas pipes unless it is specifically permitted in the regulations.”;

- in Schedule-1D, -

- under the heading “Layout of Station Facilities”, under sub-heading “(b) Distribution Pressure Regulating Station (DPRS) and Individual Pressure Regulating Station (IPRS)”, -

- after the paragraph beginning with the words and letters “In case DPRS” and ending with the words “proper cathodic protection.”, the following paragraph shall be inserted, namely: -

“In case butterfly valves are used in underground DPRS, the same shall conform to the requirements given in Annexure – I. Further, a dedicated isolation valve shall be installed upstream of such underground skid.”;

- after the paragraph beginning with the letters and slash “DPRS/IPRS” and ending with the words, brackets and figure “two (2) meters.”, the following paragraph shall be inserted, namely: -

“For Wall mounted regulating system, safety features like crash guards, caging of facilities and like other facilities shall be provided. Further, the maximum outlet pressure shall be restricted up to 2.0 bar (g).”;

- under the heading “PIPING BEYOND CONSUMER METER SET ASSEMBLY TO GAS APPLIANCE”, in the opening paragraph, for the portion beginning with the words “A metal seated” and ending with the words “location by the authorised entity”, the following shall be substituted, namely: -

“A metal seated leak detection cum excess flow shut off valve may be provided near the appliance located at easily accessible location by the authorised entity.”;

- in Annexure – I, under the heading “List of Specifications of Piping Materials used in CGD Network”, in sub-heading “Valves”, after letters, figure, and words “API 6D Pipeline Valves”, the following shall be inserted, namely: -

“API 609: Butterfly valves: Double flanged, lug-type and wafer-type;

EN 13774: Valves for gas distribution systems with maximum operating pressure less than or equal to 16 bar. Performance requirements;

BS EN 593: Industrial valves. Metallic butterfly valves for general purposes”.

VANDANA SHARMA, Secy.

[ADVT-III/4/Exty./296/2019]

Foot Note: The Principal regulations were published in the official gazette vide G.S.R. 612(E), dated the 27th August, 2008, and amended vide G.S.R. 750(E), dated 14.10.2009, F. No. M(I)/T4S/CGD/1/2010, dated 16-12-2014, F. No. L-MISC/VI/I/2007, dated 01.01.2015, F. No. M(I)/T4S/CGD/1/2010, dated 09.04.2016 and F.No. M(I)/T4S/ CGD/1/2010, dated 24.11.2016.