PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 9th March, 2016

F. No. M(1)/T4S/CGD/1/2010.– In exercise of the powers conferred by section 61 of the Petroleum and Natural Gas Regulatory Board Act, 2006 (19 of 2006), the Petroleum and Natural Gas Regulatory Board hereby makes the following regulations to amend the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, namely:

- Short title and commencement.– These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Amendment Regulations, 2016.

- They shall come into force on the date of their publication in the Official Gazette.

- In the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, -

- In Schedule 1A, under the heading “Pipes and tubing for above ground service lines up to meter set assembly”, for the words beginning with “Galvanized Iron (GI) pipes shall be used in above….” and ending with “…. above ground gas pipes.”, the following shall be substituted, namely: -

“Galvanized Iron (GI) pipes shall be used in above ground service lines up to consumer meter or meter control valve. The use of copper tubing shall only be after consumer meter such that this is not accessible to third party. GI pipes and copper tubing shall conform to the requirements given in Annexure-IV of this standard. Use of non-galvanized pipes should be restricted as far as possible; however, in case they are used they shall be properly protected and painted. PE pipe shall not be used for above ground gas pipes except for above ground risers as permitted in Schedule I D of these regulations.”;

- In Schedule 1C, under the heading “Valves and Pressure Reducing Devices”, for the words beginning with “Valves body, bonnet….” and ending with “…. used in CGD networks.”, the following shall be substituted, namely: -

“Valves body, bonnet, cover and/or end flanges components made of cast iron and / ductile iron (as per ASTM A 395) shall not be used in CGD networks. However, in case of regulators, the body or components may be made of material as permitted under the specific code as mentioned in these regulations.”;

- In Schedule 1D, under the heading “GAS SERVICE LINES”, for the sub-heading “Installation of Service Lines”, for the words beginning with “All plastic pipe and fittings ….” and ending with “…. provided in confined space.”, the following shall be substituted, namely: -

“All plastic pipe and fittings shall be laid underground and shall not be exposed.

The buried service lines shall be provided with a minimum cover of 1.0 m. Where it is impractical to provide 1.0 m cover due to physical constraints, additional protective measures such as concrete slabs or high impact resistance plastic sheets shall be installed at least 300 mm above the service line. In no case the depth of cover shall be less than 600mm.

For transition from plastic pipe to GI pipe, transition fittings shall be used. Plastic part of transition fitting protruding above ground shall be protected by encasing it with concrete guard.

In case carbon steel section beyond transition fitting is below ground, it shall be protected against corrosion by minimum 400 micron thick 2 pack high build epoxy coating.

Above ground service piping shall be Galvanized Iron or copper or carbon steel protected by anti corrosive coating.

Wherever the service line riser is installed in confined spaces like basements, only welded risers shall be used. The gap between riser and wall shall be minimum 25 mm to and shall be supported at every 2 m. Ventilators shall be provided in confined space.

Usage of PE pipes to construct above-ground risers is permitted, subject to meeting the following requirements, namely: -

- PE pipe employed shall conform to the requirements specified at Annexure 1 of these regulations;

- The PE pipe shall be used starting from a height of 3 metres from the ground level, up to which GI pipe shall be used;

- The PE pipe shall be entirely protected from exposure to sunlight and any damage due to external impact;

- The fittings employed and the jointing method for the PE riser system shall conform to the requirements of GIS / PL3: 2006 standard.”.

UPAMANYU CHATTERJEE, Secy.

[ADVT-III/4/Exty./396(188)]

Foot Note: Principal regulations were notified vide No. G.S.R. 612(E), dated 27th August, 2008, amended vide G.S.R. 750(E) dated 14-10-2009, F. No. M(I)/T4S/CGD/1/12010 dated 16-12-2014 and F. No. L0MISC/VI/I/2007 dated 01.01.2015.