# PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 15th September, 2020

F. No. PNGRB/Tech/1-T4SCGD/(1)/2020.– In exercise of the powers conferred by Section 61 of the Petroleum and Natural Gas Regulatory Board Act, 2006 (19 of 2006), the Petroleum and Natural Gas Regulatory Board hereby makes the following regulations further to amend the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, namely:-

- Short title and commencement:

- These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Second Amendment Regulations, 2020.

- They shall come into force on the date of their publication in the Official Gazette.

- In the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008, -

- In Schedule-1A, in the paragraph heading,” MATERIAL SPECIFICATIONS”, in sub-para heading, “Steel Pipe”, after the words, “Annexure-III of this standard”, the following shall be inserted, namely:

"Reinforced Thermoplastic Pipes (RTP) or Multi Layered Thermoplastic Pipes

Reinforced Thermoplastic Pipes (RTP) or multilayered thermoplastic pipes shall comply with the following requirements, namely: -

- The system in its entirety that is to say pipe, associated fittings, tools etc. shall conform to API 15S or ISO 18226 or ASME NM 1;

- Integrity of all fittings, joint, valves etc. shall commensurate with original pipeline design as per applicable standards;

- In case, the operating pressure is less than 7 Kg/cm2, all the provisions of this regulation related to the use of PE (polyethylene) pipes shall be complied with;

- If the operating pressure is greater than 7 Kg/cm2, additional protective measures for impact resistance such as concrete slabs, high impact resistance plastic sheets, steel casing shall be provided;

- The cathodic protection for steel fittings in the system shall be provided in line with the design or service life and shall be monitored for effective protection;

- Quantitative risk analysis shall be carried out by the entity for the entire system and mitigation measures shall be taken to ensure integrity of the system; and

- The proposal, for use of Reinforced Thermoplastic Pipes (RTP) or multilayered thermoplastic pipelines, shall be approved by the board of the entity with complete disclosures on associated risk.”

- In Schedule 1C, in Para (a) under the Sub-Para heading, “Fittings other than Valves and Flanges”, the words, “not exceed 0.3 and 0.5 percent respectively.”, shall be substituted by the words, “meet the requirements as per EN 1555-1, and ISO 4437-1.”

- For Schedule 1D,

- In para heading, “DESIGN INSTALLATION AND TESTING”, in sub-para heading, “CGD Network Description”;

- In point (ii) with heading, “Secondary Network”, after the word, “thermoplastic”, the word, “(PE)”, shall be inserted and the word, “(MDPE)” shall be omitted;

- In point (iii) with heading, “Tertiary Network”, the word, “(MDPE)” shall be substituted by “(PE)”.

- In Para (a), under the para heading, “VALVES”, after the words, “not be more than 3kms”, the following shall be inserted, namely:

“The inter–distance between the Sectionalising Valves in steel pipes in CGD networks outside municipal limits can be maintained as per PNGRB (Technical Standards and Specifications including safety Standards for Natural gas pipelines) Regulations, 2009 considering the location class after complying the following, namely:

- The steel pipelines in the CGD networks shall be designed considering location Class-4;

- The gas in the network is odorized and filtered; and

- Additional number of SVs shall be provided to meet the requirements as per location class in case of, the change in the population density. The assessment of location class shall be undertaken every year.”

- In Sub-Para heading, “Installation of Service Lines”, under the Paragraph heading, “GAS SERVICE LINES”, after the words beginning with, “Wherever the service line”, and ending with the words, “in confined space”, the following shall be inserted, namely: -

“In case, natural ventilation is not available, the Petroleum and Natural Gas Regulatory Board (Gas Supplies to Multi Occupancy Residential Buildings) Guidelines, 2020 and the Petroleum and Natural Gas Regulatory Board (Gas Supplies to Industrial, Commercial Customers) Guidelines, 2020. as applicable shall be adhered to."

- In Schedule 1E, under para heading, “PIPELINE SERVICE CONVERSIONS”, the word, “duel’, shall be substituted by the word, “dual” and after the word, “permitted”, the words, “unless it meets the requirements of these regulations.” Shall be inserted.

- In Annexure-II, in the Para heading, “Metering Equipment”:

- in sub-para heading, “OIML R 137-1&2”, for the words, “Gas Meters”, the words, “Thermal Mass Flow Gas Meters conforming to ISO 14511.” shall be substituted; and

- after sub-para heading “EN 12261 Gas meters”, and the entries relating thereto after the words, Turbine gas meters”, the following shall be inserted, namely:

“BS EN 14236: Ultrasonic domestic gas meters;

ISO 17089-2: Measurement of fluid flow in closed Conduits -Ultrasonic meters for gas –Part 2- Meters for industrial applications.”

VANDANA SHARMA, Secy.

[ADVT.-III/4/Exty./226/2020-21]

Foot Note: The Principal regulations were notified vide G.S.R. 612(E), dated 27.08.2008, and subsequently amended vide G.S.R. 750(E), dated 14.10.2009 and F. No. M(I)/T4S/CGD/1/2010, dated 16-12-2014 and F. No. L-MISC/VI/I/2007, dated 01.01.2015 and F. No. M(I)/T4S/CGD/1/2010, dated 09.03.2016 and F.No. M(I)/T4S/ CGD/1/2010, dated 24.11.2016 and F. No. PNGRB/Tech/1-T4SCGD/(1)/2019, dated 07.11.2019 and F. No. PNGRB/Auth/1-CGD(06)/2020, dated 30.06.2020.