PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 5th January, 2018

F. No. INFRA/PNGRB/T4S/NGPL/I/2015.–––In exercise of the powers conferred by section 61 of the Petroleum and Natural Gas Regulatory Board Act, 2006 (19 of 2006), the Petroleum and Natural Gas Regulatory Board hereby makes the following regulations to amend the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Regulations, 2009, namely:-

- Short title and commencement.

- These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Amendment Regulations, 2017.

- They shall come into force on the date of their publication in the Official Gazette.

- In the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Regulations, 2009, -

- In Appendix I, serial number 9, under the heading “Critical Infrastructure/Activity/Processes”, for the line “Environmental friendly fire extinguishing flooding system for closed space.”, the following shall be substituted namely :-

“Environmental friendly fire extinguishing system for closed space.”

- In Schedule 1D under the heading “STEEL PIPE”, para 2 under the sub-heading “Design Factor (f) and Location Classes”, beginning with “The minimum wall thickness….” and ending with “…. shall be 6.4 mm.”, the following shall be added  namely :-

"In all existing cases where thickness of pipe is less than 6.4 mm for pipe size 4 inch and above, Quantitative Risk Assessment shall be carried out and the risk level shall be reduced to as low as reasonably possible (ALARP)."

- In Schedule 1D, after the sub–heading “STEEL PIPE” and before the sub-heading “LOCATON AND LAYOUT OF PIPELINE INSTALLATIONS”, the following shall be added, namely :-

"PLASTIC PIPES AND COMPONENTS

Requirements for use of Plastic pipes as per IS 14885 or ISO 4437

- The pressure shall not exceed 7 kg/cm2 in the PE pipeline network.

- PE pipes shall be laid only in class 3 and class 4 locations.

- The PE pipeline shall be laid complying with all the provisions of the PNGRB (Technical standards and specifications including safety standards for City or local gas distribution network) Regulations, 2008.

- Clear battery limit demarcation of both spec. changes shall be done during design / construction stage.

- The material shall confirm to IS 14885 or ISO 4437 or ASTM D2513-14e1. The fittings shall as per ISO 8085 Part 3."

- In Schedule 1D under the heading “PIPELINE SYSTEM AND COMPONENT”, under the sub-heading “Other requirements”, in para 4 beginning with “Environment friendly Flooding….” and ending with “….no manning the enclosure.”, the following shall be substituted namely :-

“Environmental friendly fire extinguishing system shall be considered for control rooms, switch gear and battery room, computer rooms of compressor station, terminal station, delivery or tap off stations.”

- In Schedule 1D under the heading “TESTING AFTER CONSTRUCTION”, for the sub-heading “Test Pressure and Duration”, in

“Table 5: Minimum Test Pressure”.

| Location Class | Pressure Requirement |
| --- | --- |
| 1 | 1.25x Design Pressure |
| 2 | 1.25x Design Pressure |
| 3 | 1.40x Design Pressure |
| 4 | 1.40x Design Pressure |

the following shall be substituted namely :-

Table 5: Minimum Test Pressure

| Location Class | Pressure Requirement |
| --- | --- |
| 1 | 1.25x Design Pressure |
| 2 | 1.25x Design Pressure |
| 3 | 1.50x Design Pressure |
| 4 | 1.50x Design Pressure |

- In Schedule 1D under the heading “TESTING AFTER CONSTRUCTION” under the sub-heading, “Above Ground Station Piping”, for the words “Station piping shall be tested at minimum test pressure of 1.4 times the design pressure.”, the following shall be substituted namely :-

“Station piping shall be tested at minimum test pressure of 1.5 times the design pressure.”

VANDANA SHARMA, Secy.

[ADVT.-III/4/Exty./378/17]

Foot Note: Principal regulations were notified vide No. G.S.R. 808(E), dated 11.11.2009 and amended vide F. No. REG/T4S/NGPL/1/2012 dated 03.09.2012, F. No. REG/T4S/NGPL/1/2012 dated 14.03.2014, F. No. L-MISC/VI/I/2007 dated 01.01.2015