PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 17th July, 2020

F. No. PNGRB/Tech/2-T4SNGPL/(1)/2019. – In exercise of the powers conferred by section 61 of the Petroleum and Natural Gas Regulatory Board Act, 2006 (19 of 2006), the Petroleum and Natural Gas Regulatory Board hereby makes the following regulations further to amend the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Regulations, 2009, namely: -

- Short Title and Commencement:

- These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Amendment Regulations, 2020.

- They shall come into force on the date of their publication in the Official Gazette.

- In the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Natural Gas Pipelines) Regulations, 2009, -

- in regulation 7, after sub-regulation (1), the following sub-regulation shall be inserted, namely: -

“(1A) The Board of the concerned entity, within ninety days of the commencement of these regulations shall appoint one of its directors, who shall be responsible for ensuring compliance to these regulations.”;

- in Schedule 1A, under heading “MATERIAL SPECIFICATIONS”, for the words beginning with, “as per Line Pipe Specification” and ending with the words “conforming to (PSL 2).” under sub-heading “Steel Pipe”, the following  shall be substituted, namely:

“as per Line Pipe Specification API 5L, shall be Seamless, High Frequency Welded (HFW) including Electric Resistance Welded pipes or Longitudinal or Helical Submerged Arc Welded (SAWL/SAWH) conforming to Product Specification Level-2 (PSL 2).”;

- in Schedule1D,

- under heading “STEEL PIPE”, after sub-heading “Notes” and contents thereof, the following sub-heading and contents thereof shall be inserted, namely: -

“Transportation of Natural Gas in Class 1 and 2 locations:

- PE pipes can be laid to transport natural gas off spec gas produced from marginal or isolated fields, CBM and like other sources if it meets the following requirements, namely: -

- PE pipeline shall be laid complying with all the provisions of the PNGRB (Technical standards and specifications including safety standards for City or local gas distribution network) Regulations, 2008. These provisions inter alia include odourisation, route markers, warning mat and the likes;

- Quantitative risk analysis shall be carried out by the entity for the pipeline network and risk mitigation measures shall be taken accordingly to minimize the risk;

- The cover of 1.5 meter or the cover as specified in these Regulations for steel pipelines, whichever is higher, shall be maintained;

- The pressure shall not exceed 7 Kg/cm2 in the PE Pipeline Network;

- The material shall confirm to IS 14885 or ISO 4437 or ASTM D2513-14e1 and the fittings shall as per ISO 8085 Part 3; and

- The proposal for using PE pipelines for transportation of gas in Class 1 and 2 locations shall be approved by Board of the entity with complete disclosures on associated risk.”;

- Under heading, “PIPELINE SYSTEM AND COMPONENT”:-

- after “Table-2” the following shall be inserted , namely: -

“Note -

Block or Sectionalizing valves shall be provided at continuously accessible locations at interval distances mentioned in “Table-2”, based on predominant location class along the pipeline. Valve spacing adjustments should not exceed 10% of the applicable distance as specified in “Table-2”, so to permit a valve to be installed in a more accessible location, with continuous accessibility being the primary consideration. However, the total number of valves as per the design requirement shall remain the same.”;

- Under sub-heading “Other requirements”, for the words beginning with, “Fire and gas detectors shall be installed” and ending with the words, “the event of occurrence of fire.”, the following  shall be substituted, namely: -

“Fire and gas detectors or multi-sensor detectors shall be installed in the compressor buildings or compressors skids to initiate shut down of the unit, isolation of the compartment and release of clean agent or CO2 inside the unit in the event of occurrence of fire.”;

- in Schedule-1E, -

- Under the heading, “OPERATING AND MAINTENANCE PROCEDURE AFFECTING THE SAFETY OF GAS TRANSMISSION AND DISTRIBUTION FACILITIES”,  after the words beginning with, “The entity shall put” and ending with the words, “case of an incident.”, under the sub-heading “Essential Features of the Emergency Plan”, the following shall be inserted, namely: -

“A comprehensive ERDMP shall be developed in accordance to the Petroleum and Natural Gas Regulatory Board (Codes of Practices for Emergency Response and Disaster Management Plan (ERDMP)) Regulations, 2010. The copies of the ERDMP for the pipeline and the station specific shall be maintained at each control room along with necessary maps and records to properly administer the plan, such as the following, namely:-

- Necessary operational data;

- Pipeline patrolling records;

- Corrosion monitoring or survey records;

- Leak or tapping records;

- Routine or unusual inspection records;

- Pipeline repair records”;

- Under heading, “SAFETY AND FIRE PROTECTION”:-

- under sub-heading, “Fire and Gas Detection System”:

- under paragraph heading “Compressor stations”, for the words beginning with, “IR / Smoke detectors shall” and ending with the words, “alarm and annunciation.”, the following shall be substituted, namely: -

“IR / Smoke detectors or Multi-sensor detectors shall be provided in control room, MCC, utility room and compressor enclosure with provision of indication, alarm and annunciation.”;

- under paragraph heading, “Other Gas Installations;”, for the words beginning with, “IR / Smoke detectors shall” and ending with the words, “alarm and annunciation.”, the following shall be substituted, namely: -

“IR / Smoke detectors or Multi-sensor detectors shall be provided in control room, MCC, utility room and compressor enclosure with provision of indication, alarm and annunciation.”;

- under the sub-heading, “Fire Fighting Equipment”:

- for the words beginning with paragraph heading, “Compressor Stations”, and ending with the words, “one (1) number 2 Kg, CO2 based.”, under the paragraph heading “Gas receipt / delivery terminals”, the following shall be substituted, namely:

(a) Compressor area

One (1) number 9 kg Dry Chemical Powder (DCP) based

One (1) number 6.5 kg CO2 based per two compressors and

One (1) number mobile 75 kg DCP based.

(b) Pigging Area, Metering Area and Gas Filtration Area

One (1) number 9 kg DCP based at each location

(c)  Air compressors

One (1) number 2 kg CO2 and one number 5 kg DCP based.

(d)  Office/ Canteen/ Stores

Two (2) number 9 kg DCP based in each building.

(e)  MCC/DG Room/HT room

Two (2) number 4.5 kg CO2 based in each room or per 100 m2 floor area.

4 sand buckets with stand shall be provided near to DG room.

A trolley containing first aid fire protective accessories shall also be provided.

Intermediate pigging station:

One (1) number 75 kg and one (1) 9 Kg DCP based and one (1) number 2 kg CO2 based.

100% spares for CO2 cartridges and 50% spares for DCP cartridges shall be stored.

Sectionalizing Valve stations:

One (1) number 9 kg DCP based and one (1) number 2 kg CO2 based.

100% spares for CO2 cartridges and 50% spares for DCP cartridges shall be stored.

Gas receipt / delivery terminals:

One (1) number 75 kg and one (1) 9 kg DCP based and one (1) number 2 kg CO2 based.;

- under paragraph heading “Gas receipt / delivery terminals;”, the following words shall be omitted, namely: -

"Firefighting system with fire water network shall be provided at gas compressor stations";

- under sub headings, “The following shall also be considered:”,

- under paragraph heading “Fire Water System;”, for the words beginning with “The Fire water system” and ending with the words, “consisting of”, the following shall be substituted, namely:

"The Firefighting system with fire water network shall be provided at gas compressor stations and shall consist of:”;

- under the paragraph heading, “Design Flow Rate”: -

- for the words beginning, “The fire water pumping”, and ending with the words, “3 Lpm/m2 of area”, the following shall be substituted, namely:

“The fire water pumping requirement shall be calculated based on the highest of the spray rate given or flow through two (2) nos. of fire water monitors (i.e. 288 m3/hr) whichever is higher.  Spray rate for various areas shall be as follows:

(a) Compressor area:  20.4 Lpm/ m2 of area;

(b) Scraper area / Metering area / filter area: 10.2 Lpm/ m2 of area; and

(c)  Other area:  3 Lpm/m2 of area”

In case the any of the above facilities is within 30 meter, same shall be considered as single risk area or zone for calculation of the fire water requirement.”;

- for the words beginning with, “Compressor area, gas after cooler area,” and ending with the words, “monitors and hydrants.”, the following shall be substituted, namely: -

“Gas after cooler area, pigging area, filtration area, metering area, condensate collection area and similar other areas of the Compressor station shall be covered with medium velocity water spray system.”;

- in Annexure II, under the heading “Metering Equipment”, for the words beginning with, “AGA Report No. 9” and ending with the words, “Ultrasonic Meters.”, the following shall be substituted, namely: -

“AGA Report No. 9 Measurement of Gas by Multi-path Ultrasonic Meters and OIML R 137 Parts 1 and 2, Part1: Metrological and technical requirements, Part2: Metrological controls and performance tests”.

Vandana Sharma, Secy.

[ADVT-III/4/Exty./122/2020-21]

Foot Note: The Principal regulations were published in the Official Gazette vide No. G.S.R. 808(E), dated the 11thNovember, 2009, and amended vide F. No. REG/T4S/NGPL/1/2012, dated 03.09.2012, F. No. REG/T4S/NGPL/1/2012, dated 14.03.2014, F. No. L-MISC/VI/I/2007, dated 01.01.2015and F. No. INFRA/PNGRB/T4S/NGPL/I/2015, dated 05.01.2018.